## MED AIR SIZING
Medical Air System Sizing Worksheet
www.alliedhpi.com
Date: |  |  | Project Name:
Quantity |  | Application Description | Unit | Unit SCFM | S.U.F. % | SCFM | Cumulative SCFM
Anesthetizing Locations:
1 |  | Specialized Surgeries (Open Heart, Organ Transplant, etc.) | Room | 0.5 | 100% | 0.5 | 0.5
1 |  | Major Operating Rooms | Room | 0.5 | 100% | 0.5 | 1
1 |  | Minor Operating Room/Cysto | Room | 0.5 | 75% | 0.375 | 1.375
1 |  | Delivery Room | Room | 0.5 | 100% | 0.5 | 1.875
1 |  | Emergency Operating Room | Room | 0.5 | 25% | 0.125 | 2
1 |  | Cardiac Catherization | Room | 0.5 | 10% | 0.05 | 2.05
1 |  | Endoscopy | Room | 0.5 | 10% | 0.05 | 2.1
1 |  | Radiology | Room | 0.5 | 10% | 0.05 | 2.15
Acute Care (Non-Anesthetizing):
1 |  | Post Anesthesia Care Unit (PACU) | Bed | 2 | 25% | 0.5 | 2.65
1 |  | O. B. Recovery Room | Room | 2 | 25% | 0.5 | 3.15
1 |  | Intensive Care Units/CCU | Bed | 2 | 50% | 1 | 4.15
1 |  | Neonatal Intensive Care Units | Bed | 1.5 | 75% | 1.125 | 5.275
1 |  | Emergency Room | Bed | 2 | 10% | 0.2 | 5.475
1 |  | Ventilators | Each | 1.5 | 100% | 1.5 | 6.975
Subacute Patient Care Areas:
1 |  | Normal Nursery | Bed | 0.5 | 25% | 0.125 | 7.1
1 |  | L. D. R. P. Rooms | Room | 1 | 50% | 0.5 | 7.6
1 |  | Patient Rooms | Bed | 0.5 | 10% | 0.05 | 7.65
1 |  | Pre-Op Holding | Outlet | 1.5 | 10% | 0.15 | 7.8
1 |  | Respiratory Care Dept. | Outlet | 1.5 | 50% | 0.75 | 8.55
1 |  | Pulmonary Function Lab | Outlet | 1 | 50% | 0.5 | 9.05
1 |  | EEG & EKG | Outlet | 1 | 50% | 0.5 | 9.55
1 |  | Exam & Treatment Rooms | Room | 1 | 10% | 0.1 | 9.65
Other Areas
1 |  | Anesthesia Workroom | Room | 1.5 | 10% | 0.15 | 9.8
5 |  | Nursery Workroom | Room | 2 | 10% | 1 | 10.8
1 |  | Respiratory Care Workroom | Room | 1.5 | 10% | 0.15 | 10.95
1 |  | Equipment Repair | Outlet | 1.5 | 10% | 0.15 | 11.1
1 |  | Medical Lab | Outlet | 1 | 10% | 0.1 | 11.2
Estimated Peak Calculated SCFM Demand: | [6 empty] | 11.2 | SCFM