## MED VAC SIZING
Medical Vacuum System Sizing Worksheet
Date: | www.alliedhpi.com
Quantity |  | Application Description | Unit | Unit SCFM | S.U.F. % | SCFM | Cumulative SCFM
Anesthetizing Locations:
1 |  | Specialized Surgeries (Open Heart, Organ Transplant, etc.) | Room | 4 | 100% | 4 | 4
1 |  | Major Operating Rooms | Room | 3.5 | 100% | 3.5 | 7.5
1 |  | Endoscopy/Cystoscopy | Room | 2 | 100% | 2 | 9.5
1 |  | Delivery Room | Room | 1 | 100% | 1 | 10.5
1 |  | Emergency Operating Room | Room | 3 | 100% | 3 | 13.5
1 |  | Minor Operating Room | Room | 1 | 50% | 0.5 | 14
1 |  | Cardiac Catherization | Room | 1 | 50% | 0.5 | 14.5
1 |  | Radiology | Room | 1 | 50% | 0.5 | 15
1 |  | Waste Anesthetic Gas Evacuation | Room | 1 | 100% | 1 | 16
Acute Care (Non-Anesthetizing):
1 |  | Post-Operative Recovery Room | Bed | 1.5 | 50% | 0.75 | 16.75
1 |  | O. B. Recovery Room | Bed | 1 | 10% | 0.1 | 16.85
1 |  | Intensive Care Units | Bed | 2 | 75% | 1.5 | 18.35
1 |  | Cardiac Intensive Care Units | Bed | 1 | 50% | 0.5 | 18.85
1 |  | Neonatal Intensive Care Units | Bed | 1 | 50% | 0.5 | 19.35
1 |  | Emergency Room | Bed | 1 | 100% | 1 | 20.35
Subacute Patient Care Areas:
1 |  | Normal Nursery | Outlet | 1 | 10% | 0.1 | 20.45
1 |  | Premature Nursery | Bed | 1 | 20% | 0.2 | 20.65
1 |  | L. D. R. P. Rooms | Bed | 1 | 10% | 0.1 | 20.75
1 |  | Surgical Patient Rooms | Bed | 1.5 | 15% | 0.225 | 20.975
1 |  | Medical Patient Rooms | Bed | 1 | 10% | 0.1 | 21.075
1 |  | Observation/ Examination | Room | 1 | 10% | 0.1 | 21.175
Other Areas:
1 |  | Autopsy | Outlet | 2 | 10% | 0.2 | 21.375
1 |  | Central Supply | Outlet | 1.5 | 10% | 0.15 | 21.525
1 |  | All Others | Outlet | 1 | 10% | 0.1 | 21.625
Estimated Peak Calculated SCFM Demand: | [6 empty] | 21.625 | SCFM